PART 1 - GENERAL

  - SECTION INCLUDES

    - Expansion tanks

  - REFERENCES

    - ASME (BPV VIII, 1) - Boiler and Pressure Vessel Code, Section VIII, Division 1 - Rules for Construction of Pressure Vessels; The American Society of Mechanical Engineers; 2021.

  - SUBMITTALS

    - See Section 01300 - Administrative Requirements, for submittal procedures.

    - Product Data: Provide product data for manufactured products and assemblies required for this project. Include component sizes, rough-in requirements, service sizes, and finishes. Include product description, model and dimensions.

    - Certificates: Inspection certificates for pressure vessels from authority having jurisdiction.

    - Manufacturer's  Installation  Instructions:  Indicate  hanging  and  support  methods,  joining procedures.

    - Project Record Documents: Record actual locations of flow controls.

    - Maintenance Data: Include installation instructions, assembly views, lubrication instructions, and replacement parts list.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum five years of documented experience

  - DELIVERY, STORAGE, AND HANDLING

    - Accept valves on site in shipping containers with labeling in place. Inspect for damage.

    - Provide temporary end caps and closures on piping and fittings. Maintain in place until installation.

    - Protect piping components from entry of foreign materials by temporary covers, completing sections of the work, and isolating parts of completed system.

  - MAINTENANCE SERVICE

    - Contractor to furnish service and maintenance for one year from date of substantial completion.

  - EXTRA MATERIALS

    - See Section 01400 - Quality Requirements, for additional provisions. PART 2 - PRODUCTS

  - ASME Full Bladder Type EXPANSION TANKS

    - Manufacturers:

      - Taco, Inc; Model CA	: www.taco-hvac.com

      - ITT Bell & Gossett

      - Amtrol Inc

      - Substitutions: See Section 01600 - Product Requirements.

    - Construction: Welded steel with Stainless Steel system connection, designed, tested and stamped in accordance with ASME (BPV code sec VIII, div 1); supplied with National Board Form U-1, rated for working pressure of 125 psi , with flexible heavy duty butyl rubber bladder. [Optional 150,175,250,300PSI]. System Connections shall be two port SS construction. Two port connection arrangement shall have built in bypass to promote proper flow channeling within bladder. Bladder shall be able to accept the full volume of the expansion tank and shall be removable and replaceable. Bladder shall be NSF 61 rated for potable water service and shall be manufactured with FDA approved materials.

    - Accessories: Pressure gage (field installed by others) and air-charging fitting ; precharge to

psi.

    - Automatic Cold Water Fill Assembly (field installed by others): Pressure reducing valve, reduced pressure double check back flow preventer, test cocks, strainer, vacuum breaker, and valved by-pass.

    - Size:

      - Capacity:	HW. (acceptance volume to equal tank capacity)

      - Capacity  of  submitted  tanks  must  be  equal  to  or  greater  than  specified  units.  No exceptions unless stated in an addendum.

    - Domestic Water Heating System:

      - Select expansion tank pressure relief valve at	psi maximum.